## Sheet1
Hawaii RPS Study |  |  |  | NOTE: Kalealoa and AES heat rates and min loads were not reported in RPS study, so they were fit from data in HSIS appendix A (see bold cells) | [10 empty] | 10.0911 | 828142700
GE Energy Management Energy Consulting |  |  |  | We assign 0 heat rate to Kal3 so its output has no cost, but is considered to come from LSFO; we also set min load at 100% (all-or-nothing) since that seems to be how it's run in RPS Study; separate rules allow it only to come on when the plant is fully on. | [10 empty] | 9.9985 | [6 empty] | always use hot start, because if a plant is starting often it will be a hot start, and if not, it won't matter
8.2 Thermal Generating Characteristics | [8 empty] | min gen | 414.5 | 320.7 |  |  |  | 9.8166
Table 7: Thermal Generating Unit Properties | [14 empty] | 9.9541
Plant | Plant ID | Load Zone | Project Reporting Type | Active in Scenario 1 | Active in Scenario 2-18 | Unit Type | Primary Fuel (Scen 1) | Primary Fuel (Scen 2-18) | Max Capacity | P-Min (Scen 1) | P-Min (Scen 2-18) | Heat Rate Coef (A) | Heat Rate Coef (B) | Heat Rate Coef (C) | Full Load Heat Rate | VOM | Forced Outage Rate | Min Down Time | Min Up Time | Fixed Op. Sch. | Start Energy (Cold) | Start Energy (Hot) | FLHR | fuel cost | Full load cost | Reserve Capacity | q
|  |  |  | Y/N | Y/N |  |  |  | MW | MW | MW | MMBtu/Hr | MMBtu/MWh | MMBtu/MWh^2 | Btu/kWh | $/MWh | % | hrs | hrs | Y/N | MMBtu | MMBtu | MMBtu/MWh | $/MMBtu | $/MWh | MW | mc
AES | AES | Oahu | AES | Y | Y | Baseload | Coal | Coal | 180 | 63 | 63 | 258.75 | 14.9709 | 0.0051017 | PPA | 2 | 1.5% | N/A | N/A | Y | N/A | N/A | 17.3267 | 1.9046 | 35.0003 | 117 | 9.7 |  | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110 | 115 | 120 | 125 | 130 | 135 | 140 | 145
Kahe 1 | K1 | Oahu | Kahe | Y | N | Baseload | LSFO | Diesel | 82.1 | 32.5 | 18 | 60.278 | 8.618 | 0.009 | 10087 | 32 | 3.6% | 6 | 3 | Y | 5044 | 933 | 10.087 | 21.49 | 248.7696 | 64.1 | 60.1111 | Kahe 1 | 0 | 0 | 0 | 0 | 224.9372 | 226.8713 | 228.8054 | 230.7395 | 232.6736 | 234.6077 | 236.5418 | 238.4759 | 240.41 | 242.3441 | 244.2782 | 246.2123 | 248.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kahe 2 | K2 | Oahu | Kahe | Y | N | Baseload | LSFO | Diesel | 82.1 | 32.7 | 18.1 | 73.156 | 7.958 | 0.014 | 9990 | 32 | 3.6% | 6 | 3 | Y | 5044 | 933 | 9.99 | 21.49 | 246.6851 | 64 | 62.2143 | Kahe 2 | 0 | 0 | 0 | 0 | 215.0518 | 218.0604 | 221.069 | 224.0776 | 227.0862 | 230.0948 | 233.1034 | 236.112 | 239.1206 | 242.1292 | 245.1378 | 248.1464 | 251.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kahe 3 | K3 | Oahu | Kahe | Y | Y | Baseload | LSFO | Diesel | 86.1 | 32.3 | 17.7 | 73.462 | 7.758 | 0.014 | 9794 | 32 | 5.2% | 6 | 3 | Y | 5044 | 933 | 9.794 | 21.49 | 242.4731 | 68.4 | 69.3571 | Kahe 3 | 0 | 0 | 0 | 0 | 210.7538 | 213.7624 | 216.771 | 219.7796 | 222.7882 | 225.7968 | 228.8054 | 231.814 | 234.8226 | 237.8312 | 240.8398 | 243.8484 | 246.857 | 249.8656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kahe 4 | K4 | Oahu | Kahe | Y | Y | Baseload | LSFO | Diesel | 85.3 | 32.3 | 17.7 | 72.423 | 8.508 | 0.007 | 9933 | 32 | 5.2% | 6 | 3 | Y | 5044 | 933 | 9.933 | 21.49 | 245.4602 | 67.6 | 85.1429 | Kahe 4 | 0 | 0 | 0 | 0 | 220.8541 | 222.3584 | 223.8627 | 225.367 | 226.8713 | 228.3756 | 229.8799 | 231.3842 | 232.8885 | 234.3928 | 235.8971 | 237.4014 | 238.9057 | 240.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kahe 5 | K5 | Oahu | Kahe | Y | Y | Baseload | LSFO | Diesel | 134.3 | 50.7 | 25 | 89.066 | 8.616 | 0.003 | 9688 | 32 | 3.2% | 6 | 3 | Y | 4586 | 1352 | 9.688 | 21.49 | 240.1951 | 109.3 | 134.3 | Kahe 5 | 0 | 0 | 0 | 0 | 0 | 220.3813 | 221.026 | 221.6707 | 222.3154 | 222.9601 | 223.6048 | 224.2495 | 224.8942 | 225.5389 | 226.1836 | 226.8283 | 227.473 | 228.1177 | 228.7624 | 229.4071 | 230.0518 | 230.6965 | 231.3412 | 231.9859 | 232.6306 | 233.2753 | 233.92 | 0 | 0 | 0
Kahe 6 | K6 | Oahu | Kahe | Y | Y | Baseload | LSFO | Diesel | 134.4 | 50 | 50 | 116.696 | 8.156 | 0.008 | 10055 | 32 | 2.1% | 6 | 3 | Y | 9274 | 2703 | 10.055 | 21.49 | 248.0819 | 84.4 | 96.5 | Kahe 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224.4644 | 226.1836 | 227.9028 | 229.622 | 231.3412 | 233.0604 | 234.7796 | 236.4988 | 238.218 | 239.9372 | 241.6564 | 243.3756 | 245.0948 | 246.814 | 248.5332 | 250.2524 | 251.9716 | 0 | 0 | 0
Kalaeloa CC1 | Kal1 | Oahu | Kalaeloa | Y | Y | Baseload | LSFO | LSFO | 90 | 75 | 75 | 299.2434 | 4.4206 | 0.0093289 | PPA | 28 | 1.5% | 5 | 3 | Y | 800 | 800 | 8.5851 | 18.64 | 188.0266 | 15 | 51.8636 | Kalaeloa CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.4835 | 138.2224 | 139.9613 | 141.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kalaeloa CC2 | Kal2 | Oahu | Kalaeloa | Y | Y | Cycling | LSFO | LSFO | 90 | 75 | 75 | 299.2434 | 4.4206 | 0.0093289 | PPA | 28 | 1.5% | 5 | 3 | N | 800 | 800 | 8.5851 | 18.64 | 188.0266 | 15 | 51.55 | Kalaeloa CC2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.4835 | 138.2224 | 139.9613 | 141.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kalaeloa CC3 | Kal3 | Oahu | Kalaeloa | Y | Y | Cycling | LSFO | LSFO | 28 | 0 | 0 | 0.1 | 8.651 | 0 | PPA | 28 | 1.5% | 1 | 3 | N | 0 | 0 | 8.6546 | 18.64 | 189.3212 | 28 |  | Kalaeloa CC3 | 189.2546 | 189.2546 | 189.2546 | 189.2546 | 189.2546 | 189.2546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 7 | W7 | Oahu | Waiau | Y | Y | Baseload | LSFO | Diesel | 82.9 | 23 | 18.1 | 106.045 | 7.418 | 0.022 | 10555 | 32 | 5.2% | 6 | 3 | Y | 5044 | 933 | 10.555 | 21.49 | 258.827 | 64.8 | 385.3 | Waiau 7 | 0 | 0 | 0 | 0 | 210.324 | 215.0518 | 219.7796 | 224.5074 | 229.2352 | 233.963 | 238.6908 | 243.4186 | 248.1464 | 252.8742 | 257.602 | 262.3298 | 267.0576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 8 | W8 | Oahu | Waiau | Y | Y | Baseload | LSFO | Diesel | 86.1 | 23 | 18.1 | 63.762 | 8.669 | 0.01 | 10267 | 32 | 5.2% | 6 | 3 | Y | 5044 | 933 | 10.267 | 21.49 | 252.6378 | 68 | 103.4136 | Waiau 8 | 0 | 0 | 0 | 0 | 226.8928 | 229.0418 | 231.1908 | 233.3398 | 235.4888 | 237.6378 | 239.7868 | 241.9358 | 244.0848 | 246.2338 | 248.3828 | 250.5318 | 252.6808 | 254.8298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Honolulu 8 | H8 | Oahu | Cycling | Y | N | Cycling | LSFO | N/A | 53.4 | 22.3 | N/A | 36.3 | 10.279 | 0.006 | 11261 | 32 | 15.1% | 5 | 3 | N | 190 | 190 | 11.261 | #N/A | #N/A | #VALUE! | 488.7136 | Honolulu 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Honolulu 9 | H9 | Oahu | Cycling | Y | N | Cycling | LSFO | N/A | 54.4 | 22.3 | N/A | 69.674 | 8.921 | 0.022 | 11397 | 32 | 15.1% | 5 | 3 | N | 190 | 190 | 11.397 | #N/A | #N/A | #VALUE! |  | Honolulu 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 3 | W3 | Oahu | Cycling | Y | N | Cycling | LSFO | N/A | 46.6 | 22.3 | 22.3 | 146.083 | 4.796 | 0.085 | 11900 | 32 | 15% | 5 | 3 | N | 337 | 337 | 11.9 | #N/A | #N/A | 24.3 |  | Waiau 3 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 4 | W4 | Oahu | Cycling | Y | N | Cycling | LSFO | N/A | 46.6 | 22.3 | 22.3 | 49.306 | 9.282 | 0.032 | 11828 | 32 | 12% | 5 | 3 | N | 337 | 337 | 11.828 | #N/A | #N/A | 24.3 |  | Waiau 4 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 5 | W5 | Oahu | Cycling | Y | Y | Cycling | LSFO | Diesel | 54.5 | 22.5 | 22.5 | 60.869 | 8.786 | 0.03 | 11523 | 32 | 4.7% | 5 | 3 | N | 277 | 277 | 11.523 | 21.49 | 279.6293 | 32 |  | Waiau 5 | 0 | 0 | 0 | 0 | 0 | 253.0461 | 259.4931 | 265.9401 | 272.3871 | 278.8341 | 285.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 6 | W6 | Oahu | Cycling | Y | Y | Cycling | LSFO | Diesel | 53.5 | 22.5 | 22.5 | 63.911 | 8.713 | 0.032 | 11614 | 32 | 4.7% | 5 | 3 | N | 277 | 277 | 11.614 | 21.49 | 281.5849 | 31 |  | Waiau 6 | 0 | 0 | 0 | 0 | 0 | 253.6264 | 260.5032 | 267.38 | 274.2568 | 281.1336 | 288.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 9 | W9 | Oahu | Peaking | Y | Y | Peaking | Diesel | Diesel | 52.9 | 0 | 0 | 0 | 12.913 | 0 | 12913 | 3.75 | 10.9% | 1 | 1 | N | 36 | 36 | 12.913 | 21.49 | 281.2504 | 52.9 |  | Waiau 9 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 281.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waiau 10 | W10 | Oahu | Peaking | Y | Y | Peaking | Diesel | Diesel | 49.9 | 0 | 0 | 0 | 12.307 | 0 | 12307 | 3.98 | 10.9% | 1 | 1 | N | 33 | 33 | 12.307 | 21.49 | 268.4574 | 49.9 |  | Waiau 10 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 268.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CIP CT | CIP-CT1 | Oahu | Biodiesel | Y | Y | Peaking | Biodiesel | Biodiesel | 113 | 0 | 0 | 0 | 11.688 | 0 | 11688 | 40.76 | 15% | 1 | 1 | N | 126 | 126 | 11.688 | 45.93 | 577.5898 | 113 |  | CIP CT | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 577.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Airport DSG | AirportDG | Oahu | Biodiesel | Y | Y | Peaking | Biodiesel | Biodiesel | 8 | 0 | 0 | 0 | 10.205 | 0 | 10205 | 37.46 | 4% | 1 | 1 | N | 126 | 126 | 10.205 | 45.93 | 506.1756 | 8 |  | Airport DSG | 506.1756 | 506.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schofield | Schofield | Oahu | Biodiesel | N | Y | Peaking | N/A | Biodiesel | 48.84 | 0 | 0 | 0 | 8.894 | 0 | 8894 | 21.15 | 4% | 1 | 1 | N | 6 | 6 | 8.894 | 45.93 | 429.6514 | 48.84 |  | Schofield | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 429.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
H-Power | HPOWER | Oahu | Firm RE | Y | Y | Firm RE | Waste | Waste | 68 | N/A | N/A | PPA | PPA | PPA | PPA | 0 | N/A | N/A | N/A | Y | N/A | N/A | #VALUE! | #N/A | #VALUE! | #VALUE! |  | H-Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Honua | Honua | Oahu | Firm RE | Y | Y | Firm RE | Waste | Waste | 6 | N/A | N/A | PPA | PPA | PPA | PPA | 0 | N/A | N/A | N/A | Y | N/A | N/A | #VALUE! | #N/A | #VALUE! | #VALUE! |  | Honua | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kahului 1 | Kahului1 | Maui | Baseload | Y | N | Baseload | MSFO | N/A | 4.7 | 2.3 | N/A | 8.868 | 12.231 | 0.282 | 15445 | 1.42 | N/A | 7 | 1 | Y | 36 | 36 | 15.445 | #N/A | #N/A | #VALUE!
Kahului 2 | Kahului2 | Maui | Baseload | Y | N | Baseload | MSFO | N/A | 4.8 | 2.3 | N/A | 7.931 | 11.926 | 0.411 | 15551 | 1.22 | N/A | 7 | 1 | Y | 36 | 36 | 15.551 | #N/A | #N/A | #VALUE!
Kahului 3 | Kahului3 | Maui | Baseload | Y | N | Baseload | MSFO | N/A | 11 | 7 | N/A | 28.854 | 8.024 | 0.236 | 13249 | 1.15 | N/A | 12 | 1 | Y | 279 | 279 | 13.249 | #N/A | #N/A | #VALUE!
Kahului 4 | Kahului4 | Maui | Baseload | Y | N | Baseload | MSFO | N/A | 11.9 | 7 | N/A | 33.992 | 7.848 | 0.259 | 13786 | 1.13 | N/A | 12 | 1 | Y | 279 | 279 | 13.786 | #N/A | #N/A | #VALUE!
Maalaea CC1 | MaalaeaCC1 | Maui | Baseload | Y | Y | Baseload | Diesel | Diesel | 53 | 35 | 35 | 94.184 | 5.904 | 0.015 | 8494 | 4.7 | 0.3% | 13 | 1 | Y | 233 | 233 | 8.494 | 23.56 | 204.8186 | 18
Maalaea CC2 | MaalaeaCC2 | Maui | Baseload | Y | Y | Baseload | Diesel | Diesel | 52.8 | 35 | 18.5 | 74.108 | 7.23 | 0.006 | 8513 | 4.7 | 0.7% | 4 | 4 | Y/N | 233 | 233 | 8.513 | 23.56 | 205.2663 | 34.3
Maalaea 1 | Maalaea1 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1 | 10.288 | 23.56 | 268.0153 | #VALUE!
Maalaea 2 | Maalaea2 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1 | 10.288 | 23.56 | 268.0153 | #VALUE!
Maalaea 3 | Maalaea3 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1 | 10.288 | 23.56 | 268.0153 | #VALUE!
Maalaea 4 | Maalaea4 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 5.5 | N/A | N/A | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 1.8% | 1 | 1 | N | 5 | 5 | 10.149 | 23.56 | 266.0704 | #VALUE!
Maalaea 5 | Maalaea5 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 1.8% | 1 | 1 | N | 5 | 5 | 10.149 | 23.56 | 266.0704 | 3.6 |  | lambda
Maalaea 6 | Maalaea6 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 5.5 | N/A | N/A | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 1.8% | 1 | 1 | N | 5 | 5 | 10.149 | 23.56 | 266.0704 | #VALUE! |  | online in Fig 8, 6/23, 12:00 | 0: production; 5: switch; 10: maps
Maalaea 7 | Maalaea7 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 1.8% | 1 | 1 | N | 5 | 5 | 10.149 | 23.56 | 266.0704 | 3.6 | Cycling | W6 | 5: 22.5; 10: 47.6
Maalaea 8 | Maalaea8 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 25.624 | -2.922 | 1.477 | 9848 | 17.66 | 0.7% | 1 | 1 | N | 13 | 13 | 9.848 | 23.56 | 249.6789 | 3.6 | Kahe | K3 | 5: 405.2; 10: 380.6
Maalaea 9 | Maalaea9 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 25.624 | -2.922 | 1.477 | 9848 | 17.83 | 0.7% | 1 | 1 | N | 13 | 13 | 9.848 | 23.56 | 249.8489 | 3.6 | Kahe | K4
Maalaea 10 | Maalaea10 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.36 | 0.5% | 2 | 1 | N | 43 | 43 | 9.323 | 23.56 | 231.0099 | 4.4 | Kahe | K5
Maalaea 11 | Maalaea11 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.36 | 0.5% | 2 | 1 | N | 43 | 43 | 9.323 | 23.56 | 231.0099 | 4.4 | Kahe | K6
Maalaea 12 | Maalaea12 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.36 | 0.5% | 2 | 1 | N | 42 | 42 | 9.323 | 23.56 | 231.0099 | 4.4 | Waiau | W7 | 5: 116.9; 10: 106
Maalaea 13 | Maalaea13 | Maui | Cycling | Y | Y | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.96 | 0.5% | 2 | 1 | N | 42 | 42 | 9.323 | 23.56 | 231.6099 | 4.4 | Waiau | W8
Maalaea X1 | MaalaeaX1 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1 | 10.288 | 23.56 | 268.0153 | #VALUE!
Maalaea X2 | MaalaeaX2 | Maui | Peaking | Y | Y | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1 | 10.288 | 23.56 | 268.0153 | #VALUE! | total production, cycling and Kahe |  | 0: 427.7
New ICE 1 | NewICE1 | Maui | Biodiesel | N | Y | Peaking | N/A | Biodiesel | 16.7 | N/A | N/A | 14.68 | 6.588 | 0.052 | 8339 | 21.15 | 4% | 1 | 1 | N | 11 | 11 | 8.339 | 46.84 | 411.7488 | #VALUE!
New ICE 2 | NewICE2 | Maui | Biodiesel | N | Y | Peaking | N/A | Biodiesel | 16.7 | N/A | N/A | 14.68 | 6.588 | 0.052 | 8339 | 21.15 | 4% | 1 | 1 | N | 11 | 11 | 8.339 | 46.84 | 411.7488 | #VALUE!
HC&S | HC&S | Maui | Firm RE | Y | N | Firm RE | Biomass | N/A | 13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Y | N/A | N/A | #VALUE! | #N/A | #VALUE! | #VALUE!
Notes
[1] *Indicates a unit was assumed to retire for Scenarios 2-18
[2] **Indicates a unit was assumed to be installed for Scenarios 2-18
[3] Heat rates for AES and Kalaeloa are based on PPA contract rather than technical specifications
[4] Firm RE represent biomass and waste-to-energy plant that operate at fixed dispatch levels unless on outage
[5] Properties in this table represent the Baseline scenarios only and may have been altered for sensitivity analysis
From RPS Study Resources
2020 Fuel Prices (2013$/MMBtu) | Oahu | Maui
Biodiesel | 45.93 | 46.84
Diesel | 21.49 | 23.56
LSFO | 18.64 | 18.92
MSFO |  | 16.12
ULSD | 22.67 | 24.47
Coal | 1.9046
Note on Q7: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on Q8: 0.32 in RPS Study table, but adjusted up to get total variable cost to match Figure 30, p. 46. This also gets VO&M/fuel in the same range as Figure 11, p. 26.
Note on G13: See p. 47 of 2015 HNEI RPS Study; this is also needed to match dispatch on p. 22
Note on K14: changed from 65 to 75 based on inspection of Figs 8 & 9 of RPS Study (often runs at 75 or 150).
Note on Q14: adjusted to match total variable cost shown in RPS Study p. 46. previously used 19.6, calculated as =1000*(0.00144*(1.02^(2015-1988))+0.0138*(1.02^(2015-2004))); based on IV.B.2.v. and IV.B.3. of http://files.hawaii.gov/dcca/dca/dno/dno2005/21820.pdf previously adjusted to get correct commitment order by adding $60 to Kal1, $100 to Kal2 and $40 to Kal3
Note on N24: Originally 8.713; adjusted to make competitive with Kahe to match GE dispatch
Note on O24: originally 0.032; adjusted to make competitive with Kahe
Note on N25: Set equal to full load heat rate (instead of values from HSIS) per e-mail from John Cole 2016-09-28
Note on N26: Set equal to full load heat rate (instead of values from HSIS) per e-mail from John Cole 2016-09-28
Note on N27: Set equal to full load heat rate (instead of values from HSIS) per e-mail from John Cole 2016-09-28
Note on N28: Set equal to full load heat rate (instead of values from HSIS) per e-mail from John Cole 2016-09-28
Note on N29: Set equal to full load heat rate (instead of values from HSIS) per e-mail from John Cole 2016-09-28
Note on Q30: $0 per e-mail from John Cole 9/28/16 (waste treated as free) $18 on p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on Q31: per e-mail from John Cole 9/28/16