## main
From Table 1 of RPS Study
MW installed
Scenario | Description | Oahu_Wind | Oahu_Gen-Tie_Wind | Oahu_Central_PV | Oahu_Distributed_PV | Oahu_Biodiesel | Oahu_Firm_RE | Maui_Wind | Maui_Central_PV | Maui_Distributed_PV | Maui_Biodiesel | Maui_Firm_RE | Grid-Tie_Cable
1 | BAU - 2013 resources and practices plus committed new PV and some new dist PV | 100 | 0 | 11 | 220 |  | 74 | 72 | 0 | 40 |  | 16 | 0
2 | grid of the near future - planned new gen and retirements, better baseload turndown, ancillary svcs from central wind/solar; MATS (LSFO->diesel); cycling Maalaea CC | 100 | 0 | 11 | 220 |  | 74 | 72 | 0 | 40 |  | 0 | 0
3 |  | 100 | 0 | 200 | 260 |  | 74 | 72 | 0 | 40 |  | 0 | 0
4 |  | 200 | 0 | 200 | 260 |  | 74 | 72 | 0 | 40 |  | 0 | 0
5 |  | 300 | 0 | 200 | 260 |  | 74 | 72 | 0 | 40 |  | 0 | 0
6 |  | 100 | 0 | 300 | 360 |  | 74 | 72 | 0 | 40 |  | 0 | 0
7 |  | 200 | 0 | 300 | 360 |  | 74 | 72 | 0 | 40 |  | 0 | 0
8 |  | 200 | 0 | 400 | 460 |  | 74 | 72 | 0 | 40 |  | 0 | 0
9 |  | 200 | 0 | 300 | 560 |  | 74 | 72 | 0 | 40 |  | 0 | 0
10 |  | 100 | 200 | 200 | 260 |  | 74 | 72 | 0 | 78 |  | 0 | 0
11 |  | 100 | 0 | 200 | 260 |  | 74 | 272 | 0 | 78 |  | 0 | 200
12 |  | 100 | 200 | 200 | 260 |  | 74 | 272 | 100 | 78 |  | 0 | 200
13 |  | 100 | 200 | 300 | 360 |  | 74 | 72 | 0 | 78 |  | 0 | 0
14 |  | 100 | 0 | 300 | 360 |  | 74 | 272 | 0 | 78 |  | 0 | 200
15 |  | 100 | 200 | 300 | 360 |  | 74 | 272 | 100 | 78 |  | 0 | 200
16 |  | 200 | 200 | 400 | 460 |  | 74 | 72 | 0 | 78 |  | 0 | 0
17 |  | 200 | 0 | 400 | 460 |  | 74 | 272 | 0 | 78 |  | 0 | 200
18 |  | 200 | 200 | 400 | 460 |  | 74 | 272 | 100 | 78 |  | 0 | 200
| Oahu | [6 empty] | Maui
reported cap factor |  | 0.4088 | 0.51506 | 0.22257 | 0.18071 |  |  | 0.48713 |  | 0.18713
de-rate |  | 0.83076 | 0.83076 | 1 | 1.0071 |  |  | 1 |  | 1.0023
cap factor
Scenario | Description | Oahu_Wind | Oahu_Gen-Tie_Wind | Oahu_Central_PV | Oahu_Distributed_PV | Oahu_Biodiesel | Oahu_Firm_RE | Maui_Wind | Maui_Central_PV | Maui_Distributed_PV | Maui_Biodiesel | Maui_Firm_RE
1 |  | 0.33961 | 0.42789 | 0.22257 | 0.18223 | 0 | 0 | 0.48713 | 0.229 | 0.1875
2 |  | 0.33961 | 0.42789 | 0.22257 | 0.18223 |  |  | 0.48713 | 0.229 | 0.1875
3 |  | 0.33961 | 0.42789 | 0.22257 | 0.18146 |  |  | 0.48713 | 0.229 | 0.1875
4 |  | 0.33961 | 0.42789 | 0.22257 | 0.18146 |  |  | 0.48713 | 0.229 | 0.1875
5 |  | 0.33961 | 0.42789 | 0.22257 | 0.18146 |  |  | 0.48713 | 0.229 | 0.1875
6 |  | 0.33961 | 0.42789 | 0.22257 | 0.18227 |  |  | 0.48713 | 0.229 | 0.1875
7 |  | 0.33961 | 0.42789 | 0.22257 | 0.18227 |  |  | 0.48713 | 0.229 | 0.1875
8 |  | 0.33961 | 0.42789 | 0.22257 | 0.18225 |  |  | 0.48713 | 0.229 | 0.1875
9 |  | 0.33961 | 0.42789 | 0.22257 | 0.18222 |  |  | 0.48713 | 0.229 | 0.1875
10 |  | 0.33961 | 0.42789 | 0.22257 | 0.18146 |  |  | 0.48713 | 0.229 | 0.18762
11 |  | 0.33961 | 0.42789 | 0.22257 | 0.18146 |  |  | 0.48713 | 0.229 | 0.18762
12 |  | 0.33961 | 0.42789 | 0.22257 | 0.18146 |  |  | 0.48713 | 0.229 | 0.18762
13 |  | 0.33961 | 0.42789 | 0.22257 | 0.18227 |  |  | 0.48713 | 0.229 | 0.18762
14 |  | 0.33961 | 0.42789 | 0.22257 | 0.18227 |  |  | 0.48713 | 0.229 | 0.18762
15 |  | 0.33961 | 0.42789 | 0.22257 | 0.18227 |  |  | 0.48713 | 0.229 | 0.18762
16 |  | 0.33961 | 0.42789 | 0.22257 | 0.18225 |  |  | 0.48713 | 0.229 | 0.18762
17 |  | 0.33961 | 0.42789 | 0.22257 | 0.18225 |  |  | 0.48713 | 0.229 | 0.18762
18 |  | 0.33961 | 0.42789 | 0.22257 | 0.18225 |  |  | 0.48713 | 0.229 | 0.18762
[16 empty] | 0.2103% |  | 4.722%
Bold (pre-specified) values come from Tables 8 & 9 of RPS Study, assuming no curtailment for biodiesel, distributed solar, firm renewable, and Oahu wind in Scenarios 2, 3, 6, 11, 14)
Available GWh |  | Oahu | [5 empty] | Maui | [7 empty] | err |  | err | Figure 4 |  | Figure 3
Scenario | Description | Oahu_Wind | Oahu_Gen-Tie_Wind | Oahu_Central_PV | Oahu_Distributed_PV | Oahu_Biodiesel | Oahu_Firm_RE | Maui_Wind | Maui_Central_PV | Maui_Distributed_PV | Maui_Biodiesel | Maui_Firm_RE |  | Total production | W/S GWh available |  | pen avail (W/S/F/B) |  | W/S GWh available | pen act (W/S/B/F) | scenario | pen avail (W/S/F/B)
1 |  | 297.5 | 0 | 21.4467 | 351.2 | 12.5 | 597.1 | 307.2445 | 0 | 65.7 | 0 | 96.6 |  | 8941 | 1043.0912 | -0.3235% | 0.19565 | 2.187% | 1046.4767 | 0.18438 | 0.99685 | 0.19146
2 |  | 297.5 | 0 | 21.4467 | 351.2 | 135.4 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.2 | 1043.0912 | -0.3235% | 0.19872 | 9.8% | 1046.4767 | 0.19826 | 2.0015 | 0.18098
3 |  | 297.5 | 0 | 389.9391 | 413.3 | 102.5 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.4 | 1473.6837 | 0.06521% | 0.24321 | 6.946% | 1472.7233 | 0.24206 | 3.0076 | 0.22741
4 |  | 595 | 0 | 389.9391 | 413.3 | 90.9 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.7 | 1771.1837 | -0.09088% | 0.27519 | 5.699% | 1772.7948 | 0.2727 | 4.0151 | 0.26036
5 |  | 892.5 | 0 | 389.9391 | 413.3 | 87.9 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.5 | 2068.6837 | -0.003481% | 0.30815 | 5.309% | 2068.7557 | 0.29975 | 4.9961 | 0.29262
6 |  | 297.5 | 0 | 584.9087 | 574.8 | 79.3 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.6 | 1830.1532 | -0.01035% | 0.2805 | 5.27% | 1830.3427 | 0.27845 | 6.0007 | 0.26645
7 |  | 595 | 0 | 584.9087 | 574.8 | 71.9 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.9 | 2127.6532 | -0.03316% | 0.31294 | 4.358% | 2128.3589 | 0.30909 | 7.001 | 0.29987
8 |  | 595 | 0 | 779.8783 | 734.4 | 71.2 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.6 | 2482.2228 | 0.3467% | 0.35255 | 4.053% | 2473.6466 | 0.3426 | 8.0063 | 0.33881
9 |  | 595 | 0 | 584.9087 | 893.9 | 68.8 | 597.1 | 307.2445 | 0 | 65.7 | 0.4 | 0 |  | 8937.8 | 2446.7532 | 0.4146% | 0.3483 | 3.99% | 2436.6515 | 0.33805 | 9.0148 | 0.33494
10 |  | 297.5 | 749.6637 | 389.9391 | 413.3 | 87.3 | 597.1 | 307.2445 | 0 | 128.2 | 0.4 | 0 |  | 8962.4 | 2285.8473 | -0.213% | 0.33146 | 5.593% | 2290.7263 | 0.32896 | 10.0213 | 0.3139
11 |  | 297.5 | 0 | 389.9391 | 413.3 | 56.4 | 597.1 | 1160.7015 | 0 | 128.2 | 2.3 | 0 |  | 8973.3 | 2389.6407 | 0.09701% | 0.33939 | 3.172% | 2387.3247 | 0.33686 | 11.0237 | 0.32895
12 |  | 297.5 | 749.6637 | 389.9391 | 413.3 | 38.7 | 597.1 | 1160.7015 | 200.6044 | 128.2 | 1.6 | 0 |  | 8986.4 | 3339.9087 | -0.2161% | 0.44259 | 2.682% | 3347.1423 | 0.42567 | 12.0021 | 0.43103
13 |  | 297.5 | 749.6637 | 584.9087 | 574.8 | 75.3 | 597.1 | 307.2445 | 0 | 128.2 | 0.4 | 0 |  | 8961.1 | 2642.3169 | 0.005186% | 0.36995 | 4.625% | 2642.1799 | 0.36295 | 13.018 | 0.35359
14 |  | 297.5 | 0 | 584.9087 | 574.8 | 47.4 | 597.1 | 1160.7015 | 0 | 128.2 | 2.2 | 0 |  | 8969.2 | 2746.1102 | 0.1925% | 0.37827 | 2.633% | 2740.8335 | 0.37348 | 14.0132 | 0.36857
15 |  | 297.5 | 749.6637 | 584.9087 | 574.8 | 36.8 | 597.1 | 1160.7015 | 200.6044 | 128.2 | 1.7 | 0 |  | 8982.6 | 3696.3783 | -0.1155% | 0.48226 | 2.603% | 3700.6511 | 0.45751 | 15.0204 | 0.47003
16 |  | 595 | 749.6637 | 779.8783 | 734.4 | 68.4 | 597.1 | 307.2445 | 0 | 128.2 | 0.4 | 0 |  | 8958.3 | 3294.3865 | 0.02069% | 0.44208 | 4.013% | 3293.7049 | 0.41466 | 16.0259 | 0.42502
17 |  | 595 | 0 | 779.8783 | 734.4 | 44 | 597.1 | 1160.7015 | 0 | 128.2 | 2.1 | 0 |  | 8964.3 | 3398.1798 | 0.354% | 0.45083 | 2.493% | 3386.1927 | 0.43141 | 17.0245 | 0.43986
18 |  | 595 | 749.6637 | 779.8783 | 734.4 | 36.1 | 597.1 | 1160.7015 | 200.6044 | 128.2 | 1.8 | 0 |  | 8975.8 | 4348.4479 | 0.05609% | 0.55521 | 2.545% | 4346.0103 | 0.4982 | 18.0116 | 0.54143
cost of capital | 9.307% | <- pp 28-29: they use a fixed charge rate of 10-14% (10% for examples),
equipment life (years) | 30 | <- so we choose a lifetime and rate that give the right fixed charge rate
equipment install year | 2010 | <- installation year for all projects (dummy to keep them active and get right cost of capital)
waste plant capacity factor | 92.11%
2020 Fuel Prices (2013$/MMBtu) | Oahu | Maui |  | AES Full Load Heat Rate (as represented in RPS Study Generator Table)
Biodiesel | 45.93 | 46.84 |  | 17.3265
Diesel | 21.49 | 23.56 |  | 33
LSFO | 18.64 | 18.92
MSFO |  | 16.12
ULSD | 22.67 | 24.47
Coal | 1.9046
2020 Loads (MW) | Oahu | Maui
Peak | 1279 | 1172 | <- note: all loads now come directly from GE spreadsheets
Average | 886.8721 | 22.8311
Projects with no entry in the generator table |  |  |  |  | see "Stage 2 Hourly Renewable Shapes" for these | matches columns in Scenarios1-9.xlsx and Scenarios10-18.xlsx
Load Zone | Project Name | Generation Technology | Energy Source | Project Reporting Type | Shape ID | Column Expression
Oahu | Oahu_Wind | Wind | Wind | Wind | OAHU100W | (Oahu )?[^ ]* Wi |  |  |  | (Oahu )?[^ ]* Wi
Oahu | Oahu_Gen-Tie_Wind | Wind | Wind | Wind | LANAI200 | Lanai |  |  |  | Lanai
Oahu | Oahu_Central_PV | CentralPV | Solar | CentralPV | OAHUCENT | (Oahu )?[^ ]* Cen$ |  |  |  | (Oahu )?[^ ]* Cen
Oahu | Oahu_Distributed_PV | DistPV | Solar | DistPV | OAHUDIST | (Oahu )?[^ ]* Dis |  |  |  | (Oahu )?[^ ]* Dis
Maui | Maui_Wind | Wind | Wind | Wind | MAUI100W | (Maui )?(KWP1¦KWP2¦AUWAHI¦add'l Wi) |  |  |  | (Maui )?(KWP1¦KWP2¦AUWAHI¦add'l Wi)
Maui | Maui_Central_PV | CentralPV | Solar | CentralPV | MAUICENT | Maui .*Cent |  |  |  | Maui .*Cent
Maui | Maui_Distributed_PV | DistPV | Solar | DistPV | MAUIDIST | (Maui .*Dist¦Dist PV) |  |  |  | (Maui .*Dist¦Dist PV)
New project capital costs |  | non-zero values are from Table 3, p. 28 of RPS Study; others are assumed zero
Plant Name | Capital Cost ($/MW) | Connect Cost ($/MW)
Oahu_Wind | 2500000 | 0 |  | Note: Scenarios 2-18 have additional cost of $51M for fuel switch to diesel and $70M for lower turndown capability
Oahu_Gen-Tie_Wind | 2500000 | 2600000
Oahu_Central_PV | 3000000 | 0
Oahu_Distributed_PV | 0 | 0
Maui_Wind | 2500000 | 0
Maui_Central_PV | 3000000 | 0
Maui_Distributed_PV | 0 | 0
Schofield | 3685503.6855 | 0
New_ICE_1 | 3652694.6108 | 0
New_ICE_2 | 3652694.6108 | 0
Note on B80: based on "Assume ~$35/MWh full load cost" in message from Derek Stenclik at GE, forwarded by Jon Cole at HNEI 2016-09-28. Could instead use $30.42 energy cost (ECAC) reported in Jay Griffin correspondence

## maintenance
Thermal Units Planned Maintenance |  |  | TODO: figure out what M1415, M15116, M1718 and M1819 are in Maui listed in Table 11 but not in Table 7)
Plant ID | Start | End
H8 | 2020-03-29 00:30 | 2020-04-10 23:30 | <- retired in scenarios 2+
H9 | 2020-05-03 00:30 | 2020-06-26 23:30 | <- retired in scenarios 2+
W3 | 2020-09-18 00:30 | 2020-10-09 23:30
W4 | 2020-10-30 00:30 | 2020-11-20 23:30 | Note: we use only the hour number from the start and end periods (end hour is last hour of outage)
W5 | 2025-06-19 00:30 | 2025-07-14 23:30
W6 | 2020-08-09 00:30 | 2020-09-01 23:30
W7 | 2020-04-02 00:30 | 2020-04-21 23:30
W8 | 2020-01-26 00:30 | 2020-02-14 23:30
W9 | 2020-02-16 00:30 | 2020-04-24 23:30
W10 | 2020-05-03 00:30 | 2020-07-10 23:30
K1 | 2020-07-01 00:30 | 2020-07-22 23:30
K2 | 2020-04-23 00:30 | 2020-05-12 23:30
K3 | 2020-07-24 00:30 | 2020-10-16 23:30
K4 | 2020-05-21 00:30 | 2020-06-09 23:30
K5 | 2020-03-12 00:30 | 2020-03-31 23:30
K6 | 2020-01-02 00:30 | 2020-01-09 23:30
CIP-CT1 | 2020-07-27 00:30 | 2020-07-30 23:30
Kal1 | 2020-01-12 00:30 | 2020-01-25 23:30
Kal2 | 2020-01-19 00:30 | 2020-02-15 23:30
AES | 2020-02-17 00:30 | 2020-03-04 23:30
Kahului1 | 2020-05-18 00:30 | 2020-06-04 23:30
Kahului2 | 2020-05-04 00:30 | 2020-05-07 23:30
Kahului3 | 2020-03-02 00:30 | 2020-03-03 23:30
Kahului4 | 2020-03-16 00:30 | 2020-03-31 23:30
Kal1 | 2020-01-03 20:30 | 2020-01-04 08:30 | 6 | note: e-mail from Jon Cole 9/28/16 says Kal1 is on maintenance outage Friday evening to Saturday morning and Kal2 is on maintenance outage Saturday evening to Sunday morning
Kal2 | 2020-01-04 20:30 | 2020-01-05 08:30 | 7 | by inspection of Fig 8 (see 'figure 8 fitted data.csv'), these periods include the 8 pm hour and 8 am hour
Kal1 | 2020-01-10 20:30 | 2020-01-11 08:30
Kal2 | 2020-01-11 20:30 | 2020-01-12 08:30
Kal1 | 2020-01-17 20:30 | 2020-01-18 08:30
Kal2 | 2020-01-18 20:30 | 2020-01-19 08:30
Kal1 | 2020-01-24 20:30 | 2020-01-25 08:30
Kal2 | 2020-01-25 20:30 | 2020-01-26 08:30
Kal1 | 2020-01-31 20:30 | 2020-02-01 08:30
Kal2 | 2020-02-01 20:30 | 2020-02-02 08:30
Kal1 | 2020-02-07 20:30 | 2020-02-08 08:30
Kal2 | 2020-02-08 20:30 | 2020-02-09 08:30
Kal1 | 2020-02-14 20:30 | 2020-02-15 08:30
Kal2 | 2020-02-15 20:30 | 2020-02-16 08:30
Kal1 | 2020-02-21 20:30 | 2020-02-22 08:30
Kal2 | 2020-02-22 20:30 | 2020-02-23 08:30
Kal1 | 2020-02-28 20:30 | 2020-02-29 08:30
Kal2 | 2020-02-29 20:30 | 2020-03-01 08:30
Kal1 | 2020-03-06 20:30 | 2020-03-07 08:30
Kal2 | 2020-03-07 20:30 | 2020-03-08 08:30
Kal1 | 2020-03-13 20:30 | 2020-03-14 08:30
Kal2 | 2020-03-14 20:30 | 2020-03-15 08:30
Kal1 | 2020-03-20 20:30 | 2020-03-21 08:30
Kal2 | 2020-03-21 20:30 | 2020-03-22 08:30
Kal1 | 2020-03-27 20:30 | 2020-03-28 08:30
Kal2 | 2020-03-28 20:30 | 2020-03-29 08:30
Kal1 | 2020-04-03 20:30 | 2020-04-04 08:30
Kal2 | 2020-04-04 20:30 | 2020-04-05 08:30
Kal1 | 2020-04-10 20:30 | 2020-04-11 08:30
Kal2 | 2020-04-11 20:30 | 2020-04-12 08:30
Kal1 | 2020-04-17 20:30 | 2020-04-18 08:30
Kal2 | 2020-04-18 20:30 | 2020-04-19 08:30
Kal1 | 2020-04-24 20:30 | 2020-04-25 08:30
Kal2 | 2020-04-25 20:30 | 2020-04-26 08:30
Kal1 | 2020-05-01 20:30 | 2020-05-02 08:30
Kal2 | 2020-05-02 20:30 | 2020-05-03 08:30
Kal1 | 2020-05-08 20:30 | 2020-05-09 08:30
Kal2 | 2020-05-09 20:30 | 2020-05-10 08:30
Kal1 | 2020-05-15 20:30 | 2020-05-16 08:30
Kal2 | 2020-05-16 20:30 | 2020-05-17 08:30
Kal1 | 2020-05-22 20:30 | 2020-05-23 08:30
Kal2 | 2020-05-23 20:30 | 2020-05-24 08:30
Kal1 | 2020-05-29 20:30 | 2020-05-30 08:30
Kal2 | 2020-05-30 20:30 | 2020-05-31 08:30
Kal1 | 2020-06-05 20:30 | 2020-06-06 08:30
Kal2 | 2020-06-06 20:30 | 2020-06-07 08:30
Kal1 | 2020-06-12 20:30 | 2020-06-13 08:30
Kal2 | 2020-06-13 20:30 | 2020-06-14 08:30
Kal1 | 2020-06-19 20:30 | 2020-06-20 08:30
Kal2 | 2020-06-20 20:30 | 2020-06-21 08:30
Kal1 | 2020-06-26 20:30 | 2020-06-27 08:30
Kal2 | 2020-06-27 20:30 | 2020-06-28 08:30
Kal1 | 2020-07-03 20:30 | 2020-07-04 08:30
Kal2 | 2020-07-04 20:30 | 2020-07-05 08:30
Kal1 | 2020-07-10 20:30 | 2020-07-11 08:30
Kal2 | 2020-07-11 20:30 | 2020-07-12 08:30
Kal1 | 2020-07-17 20:30 | 2020-07-18 08:30
Kal2 | 2020-07-18 20:30 | 2020-07-19 08:30
Kal1 | 2020-07-24 20:30 | 2020-07-25 08:30
Kal2 | 2020-07-25 20:30 | 2020-07-26 08:30
Kal1 | 2020-07-31 20:30 | 2020-08-01 08:30
Kal2 | 2020-08-01 20:30 | 2020-08-02 08:30
Kal1 | 2020-08-07 20:30 | 2020-08-08 08:30
Kal2 | 2020-08-08 20:30 | 2020-08-09 08:30
Kal1 | 2020-08-14 20:30 | 2020-08-15 08:30
Kal2 | 2020-08-15 20:30 | 2020-08-16 08:30
Kal1 | 2020-08-21 20:30 | 2020-08-22 08:30
Kal2 | 2020-08-22 20:30 | 2020-08-23 08:30
Kal1 | 2020-08-28 20:30 | 2020-08-29 08:30
Kal2 | 2020-08-29 20:30 | 2020-08-30 08:30
Kal1 | 2020-09-04 20:30 | 2020-09-05 08:30
Kal2 | 2020-09-05 20:30 | 2020-09-06 08:30
Kal1 | 2020-09-11 20:30 | 2020-09-12 08:30
Kal2 | 2020-09-12 20:30 | 2020-09-13 08:30
Kal1 | 2020-09-18 20:30 | 2020-09-19 08:30
Kal2 | 2020-09-19 20:30 | 2020-09-20 08:30
Kal1 | 2020-09-25 20:30 | 2020-09-26 08:30
Kal2 | 2020-09-26 20:30 | 2020-09-27 08:30
Kal1 | 2020-10-02 20:30 | 2020-10-03 08:30
Kal2 | 2020-10-03 20:30 | 2020-10-04 08:30
Kal1 | 2020-10-09 20:30 | 2020-10-10 08:30
Kal2 | 2020-10-10 20:30 | 2020-10-11 08:30
Kal1 | 2020-10-16 20:30 | 2020-10-17 08:30
Kal2 | 2020-10-17 20:30 | 2020-10-18 08:30
Kal1 | 2020-10-23 20:30 | 2020-10-24 08:30
Kal2 | 2020-10-24 20:30 | 2020-10-25 08:30
Kal1 | 2020-10-30 20:30 | 2020-10-31 08:30
Kal2 | 2020-10-31 20:30 | 2020-11-01 08:30
Kal1 | 2020-11-06 20:30 | 2020-11-07 08:30
Kal2 | 2020-11-07 20:30 | 2020-11-08 08:30
Kal1 | 2020-11-13 20:30 | 2020-11-14 08:30
Kal2 | 2020-11-14 20:30 | 2020-11-15 08:30
Kal1 | 2020-11-20 20:30 | 2020-11-21 08:30
Kal2 | 2020-11-21 20:30 | 2020-11-22 08:30
Kal1 | 2020-11-27 20:30 | 2020-11-28 08:30
Kal2 | 2020-11-28 20:30 | 2020-11-29 08:30
Kal1 | 2020-12-04 20:30 | 2020-12-05 08:30
Kal2 | 2020-12-05 20:30 | 2020-12-06 08:30
Kal1 | 2020-12-11 20:30 | 2020-12-12 08:30
Kal2 | 2020-12-12 20:30 | 2020-12-13 08:30
Kal1 | 2020-12-18 20:30 | 2020-12-19 08:30
Kal2 | 2020-12-19 20:30 | 2020-12-20 08:30
Kal1 | 2020-12-25 20:30 | 2020-12-26 08:30
Kal2 | 2020-12-26 20:30 | 2020-12-27 08:30
Formulas:
End = [Start]+12/24
End = [End, row above]+1
Start = [Start, row above]+1

## reserves
scenario | renewable power | reserves |  | values found by inspecting RPS Study Figure 39, p. 62; see Hawaii RPS Study - reserve requirement analysis.ai
1 | 0 | 0 | <- starting point for curve
1 | 21.7796 | 17.8692 | <- nighttime max reserves (second point)
1 | 53.239 | 38.5812 | <- daytime max reserves (last point)
2 | 0 | 0
2 | 21.7796 | 17.8692
2 | 53.239 | 38.5812 |  | x | y
3 | 0 | 0 |  | 48.5753 | 43.5941
3 | 18.5878 | 17.7733 |  | 230.8056 | 180.3265
3 | 143.2717 | 102.1352 |  | 1200 | 200
4 | 0 | 0
4 | 49.2142 | 43.5305 |  | 0 | 0
4 | 145.2948 | 107.4386
5 | 0 | 0
5 | 78.5806 | 69.4338
5 | 138.439 | 118.0526
6 | 0 | 0
6 | 21.2895 | 18.075
6 | 157.8902 | 129.7395
7 | 0 | 0
7 | 48.5685 | 43.1651
7 | 182.0751 | 135.7673
8 | 0 | 0
8 | 37.2269 | 43.0394
8 | 244.1359 | 191.2669
9 | 0 | 0
9 | 48.5753 | 43.5941
9 | 230.8056 | 180.3265