## Sheet1
Hawaii RPS Study
GE Energy Management Energy Consulting
8.2 Thermal Generating Characteristics
Table 7: Thermal Generating Unit Properties
| Unit Type | Primary Fuel | Primary Fuel | Max Capacity | P-Min (Scen 1) | P-Min (Scen 2-18) | Heat Rate Coef (A) | Heat Rate Coef (B) | Heat Rate Coef (C) | Full Load Heat Rate | VOM | Forced Outage Rate % | Min Down Time | Min Up Time | Fixed Op. Sch. | Start Energy (Cold) | Start Energy (Hot)
Units |  | (Scen 1) | (Scen 2-18) | MW | MW | MW | MMBtu/Hr | Btu/kWh | Btu/kWh^2 | Btu/kWh | $/MWh | % | hrs | hrs | Y/N | MMBtu | MMBtu
AES | Baseload | Coal | Coal | 180 | 63 | 63 | PPA | PPA | PPA | PPA | N/A | 1.5% | N/A | N/A | Y | N/A | N/A
Kahe 1 | Baseload | LSFO | Diesel | 82.1 | 32.5 | 18 | 60.278 | 8.618 | 0.009 | 10087 | 0.32 | 3.6% | 6 | 3 | Y | 5044 | 933
Kahe 2 | Boselood | LSFO | Diesel | 82.1 | 32.7 | 18.1 | 73.156 | 7.958 | 0.014 | 9990 | 0.32 | 3.6% | 6 | 3 | Y | 5044 | 933
Kahle 3 | Baseload | LSFO | Diesel | 86.1 | 32.3 | 17.7 | 73.462 | 7.758 | 0.014 | 9794 | 0.32 | 5.2% | 6 | 3 | Y | 5044 | 933
Kahle 4 | Baseload | LSFO | Diesel | 85.3 | 32.3 | 17.7 | 72.423 | 8.508 | 0.007 | 9933 | 0.32 | 5.2% | 6 | 3 | Y | 5044 | 933
Kahe 5 | Baselood | LSFO | Diesel | 134.3 | 50.7 | 25 | 89.066 | 8.616 | 0.003 | 9688 | 0.32 | 3.2% | 6 | 3 | Y | 4586 | 1352
Kahe 6 | Baseload | LSFO | Diesel | 134.4 | 50 | 50 | 116.696 | 8.156 | 0.008 | 10055 | 0.32 | 2.1% | 6 | 3 | Y | 9274 | 2703
Kalaeloa CC1 | Easeload | LSFO | LSFO | 90 | 65 | 65 | PPA | PPA | PPA | PPA | N/A | 0.015 | 5 | 3 | Y | 800 | 800
Kalaeloa CC2 | Baseload | LSFO | LSFO | 90 | 65 | 65 | PPA | PPA | PPA | PPA | N/A | 0.015 | 5 | 3 | N | 800 | 800
Kolaeloa CC3 | Baselood | LSFO | LSFO | 280 | N/A | N/A | PPA | PPA | PPA | PPA | N/A | 0.015 | 1 | 3 | N | 0 | 0
Waiau 7 | Baselood | LSFO | Diesel | 82.9 | 23 | 18.1 | 106.045 | 7.418 | 0.022 | 10555 | 0.32 | 0.052 | 6 | 3 | Y | 5044 | 933
Waiau 8 | Baseload | LSFO | Diesel | 86.1 | 23 | 18.1 | 63.762 | 8.669 | 0.01 | 10267 | 0.32 | 0.052 | 6 | 3 | Y | 5044 | 933
Honolulu 8 | Cycling | LSFO | N/A | 53.4 | 22.3 | N/A | 36.3 | 10.279 | 0.006 | 11261 | 0.32 | 15.1% | 5 | 3 | N | 190 | 190
Honolulu 9 | Cycling | LSFO | N/A | 54.4 | 22.3 | N/A | 69.674 | 8.921 | 0.022 | 11397 | 0.32 | 15.1% | 5 | 3 | N | 190 | 190
Waiau 3 | Cycling | LSFO | N/A | 46.6 | 22.3 | 22.3 | 146.083 | 4.796 | 0.085 | 11900 | 0.32 | 15% | 5 | 3 | N | 337 | 337
Waiau 4 | Cycling | LSFO | N/A | 46.6 | 22.3 | 22.3 | 49.306 | 9.282 | 0.032 | 11828 | 0.32 | 0.12 | 5 | 3 | N | 337 | 337
Waiau 5 | Cycling | LSFO | Diesel | 54.5 | 22.5 | 22.5 | 60.869 | 8.786 | 0.03 | 11523 | 0.32 | 0.047 | 5 | 3 | N | 277 | 277
Waiau 6 | Cycling | LSFO | Diesel | 53.5 | 22.5 | 22.5 | 63.911 | 8.713 | 0.032 | 11614 | 0.32 | 0.047 | 5 | 3 | N | 277 | 277
Waiau 9 | Peaking | Diesel | Diesel | 52.9 | N/A | N/A | N/A | N/A | N/A | 12913 | 3.75 | 10.9% | 1 | 1 | N | 36 | 36
Waiau 10 | Peaking | Diesel | Diesel | 49.9 | N/A | N/A | N/A | N/A | N/A | 12307 | 3.98 | 10.9% | 1 | 1 | N | 33 | 33
CIP CT | Peaking | Biodiesel | Biodiesel | 113 | N/A | N/A | N/A | N/A | N/A | 11688 | 40.76 | 15% | 1 | 1 | N | 126 | 126
Airport DSG | Peaking | Biodiesel | Biodiesel | 8 | N/A | N/A | N/A | N/A | N/A | 10205 | 37.46 | 4% | 1 | 1 | N | 126 | 126
Schofield | Peaking | N/A | Biodiesel | 48.84 | N/A | N/A | N/A | N/A | N/A | 8894 | 21.15 | 4% | 1 | 1 | N | 6 | 6
H-Power | Firm RE | Waste | Waste | 68 | N/A | N/A | PPA | PPA | PPA | PPA | N/A | N/A | N/A | N/A | Y | N/A | N/A
Honua | Firm RE | Waste | Waste | 6 | N/A | N/A | PPA | PPA | PPA | PPA | N/A | N/A | N/A | N/A | Y | N/A | N/A
Kahului 1 | Baselood | MSFO | N/A | 4.7 | 2.3 | N/A | 8.868 | 12.231 | 0.282 | 15445 | 1.42 | N/A | 7 | 1 | Y | 36 | 36
Kahului 2 | Baselood | MSFO | N/A | 4.8 | 2.3 | N/A | 7.931 | 11.926 | 0.411 | 15551 | 1.22 | N/A | 7 | 1 | Y | 36 | 36
Kahului 3 | Baseload | MSFO | N/A | 11 | 7 | N/A | 28.854 | 8.024 | 0.236 | 13249 | 1.15 | N/A | 12 | 1 | Y | 279 | 279
Kahului 4 | Baselcmd | MSFO | N/A | 11.9 | 7 | N/A | 33.992 | 7.848 | 0.259 | 13786 | 1.13 | N/A | 12 | 1 | Y | 279 | 279
Maalaea CC1 | Baselood | Diesel | Diesel | 53 | 35 | 35 | 94.184 | 5.904 | 0.015 | 8494 | 4.7 | 0.003 | 13 | 1 | Y | 233 | 233
Maalaea CC2 | Baseload | Diesel | Diesel | 52.8 | 35 | 18.5 | 74.108 | 7.23 | 0.006 | 8513 | 4.7 | 0.7% | 4 | 4 | Y/N | 233 | 233
Maalaea 1 | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 0.085 | 1 | 1 | N | 1 | 1
Maalaea 2 | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 0.085 | 1 | 1 | N | 1 | 1
Maalaea 3 | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 0.085 | 1 | 1 | N | 1 | 1
Maalaea 14 | Peaking | Diesel | Diesel | 5.5 | N/A | N/A | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 0.018 | 1 | 1 | N | 5 | 5
Maalaea 5 | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 0.018 | 1 | 1 | N | 5 | 5
Maalaea 6 | Peaking | Diesel | Diesel | 5.5 | N/A | N/A | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 0.018 | 1 | 1 | N | 5 | 5
Maalaea 7 | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 18.997 | 1.18 | 1.002 | 10149 | 26.96 | 0.018 | 1 | 1 | N | 5 | 5
Maalaea 8 | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 25.624 | -2.922 | 1.477 | 9848 | 17.66 | 0.7% | 1 | 1 | N | 13 | 13
Maalaea 9 | Cycling | Diesel | Diesel | 5.5 | 1.9 | 1.9 | 25.624 | -2.922 | 1.477 | 9848 | 17.83 | 0.7% | 1 | 1 | N | 13 | 13
Maalaea 10 | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.36 | 0.5% | 2 | 1 | N | 43 | 43
Maalaea 11 | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.36 | 0.5% | 2 | 1 | N | 43 | 43
Maalaea 12 | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.36 | 0.5% | 2 | 1 | N | 42 | 42
Maalaea 13 | Cycling | Diesel | Diesel | 12.3 | 7.9 | 7.9 | 24.598 | 3.762 | 0.289 | 9323 | 11.96 | 0.5% | 2 | 1 | N | 42 | 42
Maalaea X1 | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1
Maalaea X2 | Peaking | Diesel | Diesel | 2.5 | N/A | N/A | N/A | N/A | N/A | 10288 | 25.63 | 8.5% | 1 | 1 | N | 1 | 1
New ICE | Peaking | N/A | Biodiesel | 16.7 | N/A | N/A | 14.68 | 6.588 | 0.052 | 8339 | 21.15 | 4% | 1 | 1 | N | 11 | 11
New ICE | Peaking | N/A | Biodiesel | 16.7 | N/A | N/A | 14.68 | 6.588 | 0.052 | 8339 | 21.15 | 4% | 1 | 1 | N | 11 | 11
HC&S | Firm RE | Biomass | N/A | 13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Y | N/A | N/A
Notes
[1] *Indicates a unit was assumed to retire fo Scerra dos 2-18
[2]** Indicatesa unit was assumed to be installed for Scenarios 2-18
[3]Heat rates fa r AES and Ka laeloo ore based on PPA contract rather than ipch nice I specifications
[4]Firm RE represent biomass and waste-to-energy plant that operate crtfiAed dispatch levels unless on outage
[5]Properties in this to He represent the Baseline scenatios o nly and may have been altered for se nsitivity ana lysis
0 GE Energy Consulting 59